## README
The Excel file describes the parameters of all components in the 240-bus distribution test system. The components include the equivalent source, substation transformer, lines (including line configuration), secondary distribution transformer, circuit breaker, shunt capacitor bank, and load.

## Equivalent Source
Equivalent Voltage Source
Nominal Voltage | p.u. | Voltage angle (°) | Positive-sequence resistance (Ω) | Positive-sequence reactance (Ω) | Zero-sequence resistance (Ω) | Zero-sequence reactance (Ω)
69 kV | 1 | 0 | 4.5426 | 10.5274 | 7.3655 | 24.5046

## Substation Transformer
Subtation Transformer
Name | Bus A | Bus B | kVA rating (kVA) | Primary voltage rating (kV) & Connection | Secondary voltage rating (kV) & Connection | R - % | X - %
Sub_Xfmr | eq_source_bus | bus_Xfmr | 10000 | 69 - Delta | 13.8 Gr-Wye | 0.62659 | 6.2659
Tap Changer
Name | sub_regulator_A | sub_regulator_B | sub_regulator_C
kVA rating (kVA) | 3500 | 3500 | 3500
Phase | A | B | C
Bus A | bus_Xfmr | bus_Xfmr | bus_Xfmr
Bus B | bus1 | bus1 | bus1
Connection | Grd.-Wye | Grd.-Wye | Grd.-Wye
Monitoring bus | Bus 1, Phase A | Bus 1, Phase B | Bus 1, Phase C
Primary voltage rating (kV) | 7.9677 | 7.9677 | 7.9677
Secondary voltage rating (kV) | 7.9677 | 7.9677 | 7.9677
PT ratio | 66.3953 | 66.3953 | 66.3953
Voltge setting (V) | 123 | 123 | 123
Voltage bandwidth (V) | 2 | 2 | 2
Maximum voltage limit (V) | 129 | 129 | 129
Number of taps | 32 | 32 | 32

## Line Data
Line Segment Data (Feeder A) | [5 empty] | Line Segment Data (Feeder B) | [5 empty] | Line Segment Data (Feeder C)
Name | Bus A | Bus B | Length(ft.) | Phases | Config. | Name | Bus A | Bus B | Length(ft.) | Phase | Config. | Name | Bus A | Bus B | Length(ft.) | Phase | Config.
L_1001_1002 | 1001 | 1002 | 2967 | ABC | UG_3p_type1 | L_2001_2002 | 2001 | 2002 | 1388 | ABC | UG_3p_type1 | L_3001_3003 | 3001 | 3003 | 2307 | ABC | UG_3p_type1
L_1002_1003 | 1002 | 1003 | 372 | ABC | UG_3p_type2 | L_2002_2003 | 2002 | 2003 | 1281 | ABC | OH_3p_type1 | L_3003_3002 | 3003 | 3002 | 85 | ABC | UG_3p_type2
L_1002_1004 | 1002 | 1004 | 638 | ABC | OH_3p_type1 | L_2003_2004 | 2003 | 2004 | 798 | ABC | OH_3p_type1 | L_3003_3004 | 3003 | 3004 | 81 | ABC | UG_3p_type2
L_1004_1005 | 1004 | 1005 | 394 | ABC | OH_3p_type1 | L_2004_2005 | 2004 | 2005 | 317 | ABC | OH_3p_type1 | L_3003_3005 | 3003 | 3005 | 1997 | ABC | UG_3p_type1
L_1005_1006 | 1005 | 1006 | 1049 | ABC | OH_3p_type1 | L_2005_2006 | 2005 | 2006 | 145 | ABC | OH_3p_type1 | L_3005_3006 | 3005 | 3006 | 311 | ABC | OH_3p_type1
L_1006_1007 | 1006 | 1007 | 2000 | AB | OH_2p_type2 | L_2006_2007 | 2006 | 2007 | 245 | A | OH_1p_type5 | L_3006_3007 | 3006 | 3007 | 370 | ABC | OH_3p_type1
L_1006_1008 | 1006 | 1008 | 454 | ABC | OH_3p_type1 | L_2007_2008 | 2007 | 2008 | 125 | A | UG_1p_type2 | L_3005_3008 | 3005 | 3008 | 136 | ABC | OH_3p_type1
L_1008_1009 | 1008 | 1009 | 1082 | ABC | OH_3p_type1 | L_2007_2009 | 2007 | 2009 | 161 | A | OH_1p_type2 | L_3008_3009 | 3008 | 3009 | 161 | A | OH_1p_type5
L_1009_1010 | 1009 | 1010 | 169 | ABC | OH_3p_type1 | L_2006_2010 | 2006 | 2010 | 170 | ABC | OH_3p_type1 | L_3009_3010 | 3009 | 3010 | 347 | A | OH_1p_type5
L_1009_1011 | 1009 | 1011 | 60 | ABC | UG_3p_type2 | L_2010_2011 | 2010 | 2011 | 275 | ABC | OH_3p_type1 | L_3010_3011 | 3010 | 3011 | 265 | A | OH_1p_type5
L_1011_1012 | 1011 | 1012 | 60 | ABC | UG_3p_type2 | L_2011_2012 | 2011 | 2012 | 503 | ABC | OH_3p_type1 | L_3011_3012 | 3011 | 3012 | 312 | A | OH_1p_type5
L_1012_1013 | 1012 | 1013 | 306 | ABC | UG_3p_type2 | L_2013_2014 | 2013 | 2014 | 268 | ABC | OH_3p_type1 | L_3008_3013 | 3008 | 3013 | 170 | B | OH_1p_type5
L_1013_1014 | 1013 | 1014 | 208 | B | UG_1p_type2 | L_2014_2015 | 2014 | 2015 | 120 | B | UG_1p_type2 | L_3013_3014 | 3013 | 3014 | 295 | B | OH_1p_type5
L_1014_1015 | 1014 | 1015 | 126 | B | UG_1p_type2 | L_2014_2016 | 2014 | 2016 | 257 | ABC | OH_3p_type1 | L_3008_3015 | 3008 | 3015 | 322 | ABC | OH_3p_type1
L_1013_1016 | 1013 | 1016 | 468 | C | UG_1p_type2 | L_2016_2017 | 2016 | 2017 | 174 | ABC | UG_3p_type2 | L_3015_3016 | 3015 | 3016 | 210 | B | OH_1p_type5
L_1016_1017 | 1016 | 1017 | 71 | C | UG_1p_type2 | L_2017_2018 | 2017 | 2018 | 447 | ABC | UG_3p_type2 | L_3016_3017 | 3016 | 3017 | 259 | B | OH_1p_type5
[6 empty] | L_2013_2019 | 2013 | 2019 | 45 | ABC | OH_3p_type1 | L_3015_3018 | 3015 | 3018 | 181 | C | OH_1p_type5
[6 empty] | L_2019_2020 | 2019 | 2020 | 642 | B | UG_1p_type2 | L_3018_3019 | 3018 | 3019 | 281 | C | OH_1p_type5
[6 empty] | L_2019_2021 | 2019 | 2021 | 43 | ABC | OH_3p_type1 | L_3019_3020 | 3019 | 3020 | 307 | C | OH_1p_type5
[6 empty] | L_2021_2022 | 2021 | 2022 | 205 | C | UG_1p_type2 | L_3020_3021 | 3020 | 3021 | 303 | C | OH_1p_type5
[6 empty] | L_2022_2023 | 2022 | 2023 | 150 | C | UG_1p_type2 | L_3015_3022 | 3015 | 3022 | 289 | ABC | OH_3p_type1
[6 empty] | L_2023_2024 | 2023 | 2024 | 408 | C | UG_1p_type2 | L_3022_3023 | 3022 | 3023 | 181 | A | OH_1p_type5
[6 empty] | L_2024_2025 | 2024 | 2025 | 331 | C | UG_1p_type2 | L_3023_3024 | 3023 | 3024 | 320 | A | OH_1p_type5
[6 empty] | L_2026_2027 | 2026 | 2027 | 369 | ABC | OH_3p_type1 | L_3024_3025 | 3024 | 3025 | 331 | A | OH_1p_type5
[6 empty] | L_2027_2028 | 2027 | 2028 | 285 | ABC | UG_3p_type2 | L_3022_3026 | 3022 | 3026 | 164 | A | OH_1p_type5
[6 empty] | L_2028_2029 | 2028 | 2029 | 131 | ABC | UG_3p_type2 | L_3026_3027 | 3026 | 3027 | 368 | A | OH_1p_type5
[6 empty] | L_2029_2030 | 2029 | 2030 | 165 | ABC | UG_3p_type2 | L_3027_3028 | 3027 | 3028 | 241 | A | OH_1p_type5
[6 empty] | L_2030_2031 | 2030 | 2031 | 245 | ABC | UG_3p_type2 | L_3028_3029 | 3028 | 3029 | 317 | A | OH_1p_type5
[6 empty] | L_2027_2032 | 2027 | 2032 | 149 | ABC | OH_3p_type1 | L_3022_3030 | 3022 | 3030 | 304 | ABC | OH_3p_type1
[6 empty] | L_2032_2033 | 2032 | 2033 | 289 | ABC | OH_3p_type1 | L_3030_3035 | 3030 | 3035 | 103 | ABC | OH_3p_type1
[6 empty] | L_2033_2034 | 2033 | 2034 | 185 | ABC | OH_3p_type5 | L_3035_3036 | 3035 | 3036 | 271 | ABC | OH_3p_type1
[6 empty] | L_2033_2035 | 2033 | 2035 | 160 | ABC | OH_3p_type1 | L_3036_3037 | 3036 | 3037 | 136 | ABC | OH_3p_type1
[6 empty] | L_2035_2036 | 2035 | 2036 | 160 | ABC | OH_3p_type1 | L_3037_3038 | 3037 | 3038 | 252 | ABC | OH_3p_type1
[6 empty] | L_2036_2037 | 2036 | 2037 | 80 | ABC | OH_3p_type1 | L_3038_3039 | 3038 | 3039 | 235 | ABC | OH_3p_type1
[6 empty] | L_2037_2038 | 2037 | 2038 | 192 | ABC | OH_3p_type1 | L_3039_3053 | 3039 | 3053 | 263 | ABC | OH_3p_type1
[6 empty] | L_2038_2039 | 2038 | 2039 | 800 | ABC | OH_3p_type1 | L_3053_3054 | 3053 | 3054 | 280 | ABC | UG_3p_type2
[6 empty] | L_2039_2040 | 2039 | 2040 | 309 | ABC | OH_3p_type1 | L_3053_3055 | 3053 | 3055 | 1335 | B | UG_1p_type2
[6 empty] | L_2040_2041 | 2040 | 2041 | 383 | ABC | OH_3p_type1 | L_3055_3056 | 3055 | 3056 | 128 | B | UG_1p_type2
[6 empty] | L_2039_2042 | 2039 | 2042 | 35 | ABC | UG_3p_type2 | L_3056_3057 | 3056 | 3057 | 178 | B | UG_1p_type2
[6 empty] | L_2042_2043 | 2042 | 2043 | 158 | ABC | UG_3p_type2 | L_3057_3058 | 3057 | 3058 | 178 | B | UG_1p_type2
[6 empty] | L_2043_2044 | 2043 | 2044 | 342 | ABC | UG_3p_type2 | L_3058_3059 | 3058 | 3059 | 274 | B | UG_1p_type2
[6 empty] | L_2044_2045 | 2044 | 2045 | 323 | B | UG_1p_type2 | L_3059_3060 | 3059 | 3060 | 77 | B | UG_1p_type2
[6 empty] | L_2045_2046 | 2045 | 2046 | 330 | B | UG_1p_type2 | L_3060_3061 | 3060 | 3061 | 184 | B | UG_1p_type2
[6 empty] | L_2045_2047 | 2045 | 2047 | 189 | B | UG_1p_type2 | L_3055_3062 | 3055 | 3062 | 443 | B | UG_1p_type2
[6 empty] | L_2047_2048 | 2047 | 2048 | 259 | B | UG_1p_type2 | L_3062_3063 | 3062 | 3063 | 198 | B | UG_1p_type2
[6 empty] | L_2044_2049 | 2044 | 2049 | 130 | ABC | UG_3p_type2 | L_3063_3064 | 3063 | 3064 | 157 | B | UG_1p_type2
[6 empty] | L_2049_2050 | 2049 | 2050 | 124 | ABC | UG_3p_type2 | L_3064_3065 | 3064 | 3065 | 205 | B | UG_1p_type2
[6 empty] | L_2050_2051 | 2050 | 2051 | 139 | ABC | UG_3p_type2 | L_3065_3066 | 3065 | 3066 | 123 | B | UG_1p_type2
[6 empty] | L_2051_2052 | 2051 | 2052 | 134 | ABC | UG_3p_type2 | L_3066_3067 | 3066 | 3067 | 274 | B | UG_1p_type2
[6 empty] | L_2044_2053 | 2044 | 2053 | 464 | ABC | UG_3p_type2 | L_3030_3040 | 3030 | 3040 | 332 | ABC | OH_3p_type1
[6 empty] | L_2053_2054 | 2053 | 2054 | 139 | ABC | UG_3p_type2 | L_3040_3044 | 3040 | 3044 | 144 | C | OH_1p_type5
[6 empty] | L_2054_2055 | 2054 | 2055 | 156 | ABC | UG_3p_type2 | L_3044_3045 | 3044 | 3045 | 393 | C | OH_1p_type5
[6 empty] | L_2055_2056 | 2055 | 2056 | 204 | ABC | UG_3p_type2 | L_3040_3041 | 3040 | 3041 | 121 | C | OH_1p_type5
[6 empty] | L_2053_2057 | 2053 | 2057 | 761 | ABC | UG_3p_type2 | L_3041_3042 | 3041 | 3042 | 328 | C | OH_1p_type5
[6 empty] | L_2057_2058 | 2057 | 2058 | 407 | ABC | UG_3p_type2 | L_3042_3043 | 3042 | 3043 | 418 | C | OH_1p_type5
[6 empty] | L_2057_2059 | 2057 | 2059 | 685 | ABC | UG_3p_type2 | L_3040_3046 | 3040 | 3046 | 329 | ABC | OH_3p_type1
[6 empty] | L_2059_2060 | 2059 | 2060 | 304 | ABC | UG_3p_type2 | L_3046_3047 | 3046 | 3047 | 219 | ABC | OH_3p_type1
[12 empty] | L_3046_3048 | 3046 | 3048 | 130 | ABC | OH_3p_type1
[12 empty] | L_3048_3049 | 3048 | 3049 | 226 | ABC | OH_3p_type1
[12 empty] | L_3049_3050 | 3049 | 3050 | 167 | ABC | OH_3p_type1
[12 empty] | L_3050_3051 | 3050 | 3051 | 360 | ABC | OH_3p_type1
[12 empty] | L_3051_3052 | 3051 | 3052 | 292 | ABC | OH_3p_type1
[12 empty] | L_3030_3031 | 3030 | 3031 | 243 | ABC | OH_3p_type1
[12 empty] | L_3031_3032 | 3031 | 3032 | 251 | ABC | OH_3p_type1
[12 empty] | L_3032_3033 | 3032 | 3033 | 388 | ABC | OH_3p_type1
[12 empty] | L_3033_3034 | 3033 | 3034 | 257 | ABC | OH_3p_type1
[12 empty] | L_3034_3068 | 3034 | 3068 | 164 | ABC | OH_3p_type1
[12 empty] | L_3068_3069 | 3068 | 3069 | 329 | ABC | OH_3p_type1
[12 empty] | L_3069_3070 | 3069 | 3070 | 107 | ABC | UG_3p_type2
[12 empty] | L_3070_3071 | 3070 | 3071 | 141 | ABC | UG_3p_type2
[12 empty] | L_3071_3072 | 3071 | 3072 | 90 | ABC | UG_3p_type2
[12 empty] | L_3069_3073 | 3069 | 3073 | 20 | ABC | OH_3p_type1
[12 empty] | L_3073_3074 | 3073 | 3074 | 340 | ABC | OH_3p_type1
[12 empty] | L_3068_3075 | 3068 | 3075 | 188 | ABC | OH_3p_type1
[12 empty] | L_3076_3077 | 3076 | 3077 | 877 | ABC | OH_3p_type1
[12 empty] | L_3077_3078 | 3077 | 3078 | 80 | ABC | OH_3p_type1
[12 empty] | L_3076_3079 | 3076 | 3079 | 191 | ABC | OH_3p_type1
[12 empty] | L_3079_3080 | 3079 | 3080 | 604 | ABC | OH_3p_type1
[12 empty] | L_3080_3081 | 3080 | 3081 | 195 | ABC | OH_3p_type1
[12 empty] | L_3080_3082 | 3080 | 3082 | 540 | ABC | OH_3p_type1
[12 empty] | L_3082_3083 | 3082 | 3083 | 125 | A | UG_1p_type2
[12 empty] | L_3083_3084 | 3083 | 3084 | 196 | A | UG_1p_type2
[12 empty] | L_3084_3085 | 3084 | 3085 | 515 | A | UG_1p_type2
[12 empty] | L_3085_3086 | 3085 | 3086 | 338 | A | UG_1p_type2
[12 empty] | L_3086_3087 | 3086 | 3087 | 239 | A | UG_1p_type2
[12 empty] | L_3087_3088 | 3087 | 3088 | 420 | A | UG_1p_type2
[12 empty] | L_3088_3089 | 3088 | 3089 | 112 | A | UG_1p_type2
[12 empty] | L_3089_3090 | 3089 | 3090 | 565 | A | UG_1p_type2
[12 empty] | L_3090_3091 | 3090 | 3091 | 222 | A | UG_1p_type2
[12 empty] | L_3082_3092 | 3082 | 3092 | 185 | ABC | UG_3p_type2
[12 empty] | L_3092_3093 | 3092 | 3093 | 230 | A | UG_1p_type2
[12 empty] | L_3093_3094 | 3093 | 3094 | 125 | A | UG_1p_type2
[12 empty] | L_3094_3095 | 3094 | 3095 | 65 | A | UG_1p_type2
[12 empty] | L_3095_3096 | 3095 | 3096 | 296 | A | UG_1p_type2
[12 empty] | L_3096_3097 | 3096 | 3097 | 117 | A | UG_1p_type2
[12 empty] | L_3092_3098 | 3092 | 3098 | 284 | B | UG_1p_type2
[12 empty] | L_3098_3099 | 3098 | 3099 | 368 | B | UG_1p_type2
[12 empty] | L_3092_3100 | 3092 | 3100 | 91 | ABC | UG_3p_type2
[12 empty] | L_3100_3101 | 3100 | 3101 | 157 | C | UG_1p_type2
[12 empty] | L_3101_3102 | 3101 | 3102 | 225 | C | UG_1p_type2
[12 empty] | L_3102_3103 | 3102 | 3103 | 134 | C | UG_1p_type2
[12 empty] | L_3100_3104 | 3100 | 3104 | 223 | C | UG_1p_type2
[12 empty] | L_3104_3105 | 3104 | 3105 | 120 | C | UG_1p_type2
[12 empty] | L_3105_3106 | 3105 | 3106 | 181 | C | UG_1p_type2
[12 empty] | L_3082_3107 | 3082 | 3107 | 1461 | ABC | UG_3p_type1
[12 empty] | L_3107_3108 | 3107 | 3108 | 466 | A | UG_1p_type2
[12 empty] | L_3108_3109 | 3108 | 3109 | 136 | A | UG_1p_type2
[12 empty] | L_3109_3110 | 3109 | 3110 | 152 | A | UG_1p_type2
[12 empty] | L_3110_3111 | 3110 | 3111 | 276 | A | UG_1p_type2
[12 empty] | L_3111_3112 | 3111 | 3112 | 328 | A | UG_1p_type2
[12 empty] | L_3107_3113 | 3107 | 3113 | 245 | B | UG_1p_type2
[12 empty] | L_3113_3114 | 3113 | 3114 | 149 | B | UG_3p_type2
[12 empty] | L_3114_3115 | 3114 | 3115 | 331 | B | UG_1p_type2
[12 empty] | L_3113_3116 | 3113 | 3116 | 456 | B | UG_1p_type2
[12 empty] | L_3116_3117 | 3116 | 3117 | 112 | B | UG_1p_type2
[12 empty] | L_3107_3118 | 3107 | 3118 | 2267 | ABC | UG_3p_type1
[12 empty] | L_3118_3119 | 3118 | 3119 | 464 | B | UG_1p_type2
[12 empty] | L_3119_3120 | 3119 | 3120 | 350 | B | UG_1p_type2
[12 empty] | L_3120_3121 | 3120 | 3121 | 206 | B | UG_1p_type2
[12 empty] | L_3121_3122 | 3121 | 3122 | 177 | B | UG_1p_type2
[12 empty] | L_3119_3123 | 3119 | 3123 | 91 | B | UG_1p_type2
[12 empty] | L_3123_3124 | 3123 | 3124 | 67 | B | UG_1p_type2
[12 empty] | L_3124_3125 | 3124 | 3125 | 151 | B | UG_1p_type2
[12 empty] | L_3125_3126 | 3125 | 3126 | 343 | B | UG_1p_type2
[12 empty] | L_3126_3127 | 3126 | 3127 | 234 | B | UG_1p_type2
[12 empty] | L_3127_3128 | 3127 | 3128 | 238 | B | UG_1p_type2
[12 empty] | L_3128_3129 | 3128 | 3129 | 243 | B | UG_1p_type2
[12 empty] | L_3129_3130 | 3129 | 3130 | 230 | B | UG_1p_type2
[12 empty] | L_3130_3131 | 3130 | 3131 | 194 | B | UG_1p_type2
[12 empty] | L_3118_3132 | 3118 | 3132 | 501 | A | UG_1p_type2
[12 empty] | L_3132_3133 | 3132 | 3133 | 145 | A | UG_1p_type2
[12 empty] | L_3133_3134 | 3133 | 3134 | 281 | A | UG_1p_type2
[12 empty] | L_3134_3135 | 3134 | 3135 | 240 | A | UG_1p_type2
[12 empty] | L_3135_3136 | 3135 | 3136 | 367 | A | UG_1p_type2
[12 empty] | L_3133_3137 | 3133 | 3137 | 252 | A | UG_1p_type2
[12 empty] | L_3137_3138 | 3137 | 3138 | 351 | A | UG_1p_type2
[12 empty] | L_3138_3139 | 3138 | 3139 | 289 | A | UG_1p_type2
[12 empty] | L_3107_3140 | 3107 | 3140 | 255 | C | UG_1p_type2
[12 empty] | L_3140_3141 | 3140 | 3141 | 134 | C | UG_1p_type2
[12 empty] | L_3141_3142 | 3141 | 3142 | 193 | C | UG_1p_type2
[12 empty] | L_3142_3143 | 3142 | 3143 | 202 | C | UG_1p_type2
[12 empty] | L_3140_3148 | 3140 | 3148 | 147 | C | UG_1p_type2
[12 empty] | L_3148_3149 | 3148 | 3149 | 253 | C | UG_1p_type2
[12 empty] | L_3149_3150 | 3149 | 3150 | 139 | C | UG_1p_type2
[12 empty] | L_3150_3151 | 3150 | 3151 | 156 | C | UG_1p_type2
[12 empty] | L_3151_3152 | 3151 | 3152 | 260 | C | UG_1p_type2
[12 empty] | L_3152_3153 | 3152 | 3153 | 139 | C | UG_1p_type2
[12 empty] | L_3153_3154 | 3153 | 3154 | 119 | C | UG_1p_type2
[12 empty] | L_3154_3155 | 3154 | 3155 | 505 | C | UG_1p_type2
[12 empty] | L_3140_3156 | 3140 | 3156 | 319 | C | UG_1p_type2
[12 empty] | L_3156_3144 | 3156 | 3144 | 122 | C | UG_1p_type2
[12 empty] | L_3144_3145 | 3144 | 3145 | 178 | C | UG_1p_type2
[12 empty] | L_3145_3146 | 3145 | 3146 | 178 | C | UG_1p_type2
[12 empty] | L_3146_3147 | 3146 | 3147 | 178 | C | UG_1p_type2
[12 empty] | L_3156_3157 | 3156 | 3157 | 153 | C | UG_1p_type2
[12 empty] | L_3157_3158 | 3157 | 3158 | 295 | C | UG_1p_type2
[12 empty] | L_3158_3159 | 3158 | 3159 | 257 | C | UG_1p_type2
[12 empty] | L_3159_3160 | 3159 | 3160 | 243 | C | UG_1p_type2
[12 empty] | L_3160_3161 | 3160 | 3161 | 237 | C | UG_1p_type2
[12 empty] | L_3161_3162 | 3161 | 3162 | 176 | C | UG_1p_type2

## Line Configuration
Configuration 1: OH_3p_type1
Rmatrix (Ω/mile) | 0.61593 | 0.17093 | 0.17093
| 0.17093 | 0.61593 | 0.17093
| 0.17093 | 0.17093 | 0.61593
Xmatrix (Ω/mile) | 1.2094 | 0.43319 | 0.43319
| 0.43319 | 1.2094 | 0.43319
| 0.43319 | 0.43319 | 1.2094
Size | 4/0
Material | ACSR
Current Carrying Capacity (A) | 340
Resistance @ 25 °C (Ω/mile) | 0.445
Resistance @ 50 °C (Ω/mile) | 0.592
Geometric Mean Radisu (ft) | 0.00814
Conductor Diameter (in) | 0.563
Preferred Neutral | #2/0 ACSR 6/1
Construction | 1
Configuration 2: OH_2p_type2
Rmatrix (Ω/mile) | 0.58925 | 0.1695
| 0.1695 | 0.58925
Xmatrix (Ω/mile) | 1.0749 | 0.38788
| 0.38788 | 1.0749
Size | #4/0
Material | ACSR
Current Carrying Capacity (A) | 357
Resistance @ 25 °C (Ω/mile) | 0.41976
Resistance @ 50 °C (Ω/mile) | 0.62832
Geometric Mean Radisu (ft) | 0.0255
Conductor Diameter (in) | 0.502
Preferred Neutral | #2/0 ACSR 6/1
Construction | 2
Configuration 3: OH_1p_type2
Rmatrix (Ω/mile) | 0.59247
Xmatrix (Ω/mile) | 1.0658
Size | #4/0
Material | ACSR
Current Carrying Capacity (A) | 357
Resistance @ 25 °C (Ω/mile) | 0.41976
Resistance @ 50 °C (Ω/mile) | 0.62832
Geometric Mean Radisu (ft) | 0.0255
Conductor Diameter (in) | 0.502
Preferred Neutral | #2/0 ACSR 6/1
Construction | 2
Configuration 1: OH_3p_type5
Rmatrix (Ω/mile) | 1.1916 | 0.23485 | 0.23485
| 0.23485 | 1.1916 | 0.23485
| 0.23485 | 0.23485 | 1.1916
Xmatrix (Ω/mile) | 1.2095 | 0.48926 | 0.48926
| 0.48926 | 1.2095 | 0.48926
| 0.48926 | 0.48926 | 1.2095
Size | 1/0
Material | ACSR
Current Carrying Capacity (A) | 242
Resistance @ 25 °C (Ω/mile) | 0.95675
Resistance @ 50 °C (Ω/mile) | 1.0513
Geometric Mean Radisu (ft) | 0.012915
Conductor Diameter (in) | 0.398
Preferred Neutral | 1 ACSR 6/1
Construction | 1
Configuration 3: OH_1p_type5
Rmatrix (Ω/mile) | 1.1943
Xmatrix (Ω/mile) | 1.2054
Size | 1/0
Material | ACSR
Current Carrying Capacity (A) | 242
Resistance @ 25 °C (Ω/mile) | 0.95675
Resistance @ 50 °C (Ω/mile) | 1.0513
Geometric Mean Radisu (ft) | 0.012915
Conductor Diameter (in) | 0.398
Preferred Neutral | 1 ACSR 6/1
Construction | 1
Configuration 4: UG_3p_type1
Rmatrix (Ω/mile) | 1.0094 | 0.40973 | 0.40973
| 0.40973 | 1.0094 | 0.40973
| 0.40973 | 0.40973 | 1.0094
Xmatrix (Ω/mile) | 0.49316 | 0.10085 | 0.10085
| 0.10085 | 0.49316 | 0.10085
| 0.10085 | 0.10085 | 0.49316
Cmatrix (nF/mile) | 286.1016 | 0 | 0
| 0 | 286.1016 | 0
| 0 | 0 | 286.1016
Size | 4/0
Material | AA
Current Carrying Capacity of Conductor (A) | 326
Phase Conductor Resistance (Ω/1000 ft) | 0.105
Geometric Mean Radisu of Phase Conductor (ft) | 0.0167
Type Neutral | Concentric
Equivalent Resistance Concentric Neutral (Ω/1000 ft) | 0.3
Number of Strands | 11
Outside Diamter of Cable Including Neutral (in) | 1.218
Diameter Under Neutral (Over Screen) (in) | 1.09
Outside Diamter of Cable Insulation (Under Screen) (in) | 1.01
Diameter of Conductor (in) | 0.512
Dielectric Constant of Insulation | 2.75
Construction Type | 1
Configuration 5: UG_3p_type2
Rmatrix (Ω/mile) | 1.6926 | 0.55009 | 0.55009
| 0.55009 | 1.6926 | 0.55009
| 0.55009 | 0.55009 | 1.6926
Xmatrix (Ω/mile) | 0.79176 | 0.34493 | 0.34493
| 0.34493 | 0.79176 | 0.34493
| 0.34493 | 0.34493 | 0.79176
Cmatrix (nF/mile) | 207.8805 | 0 | 0
| 0 | 207.8805 | 0
| 0 | 0 | 207.8805
Size | 1/0
Material | AA
Current Carrying Capacity of Conductor (A) | 228
Phase Conductor Resistance (Ω/1000 ft) | 0.211
Geometric Mean Radisu of Phase Conductor (ft) | 0.111
Type Neutral | Concentric
Equivalent Resistance Concentric Neutral (Ω/1000 ft) | 0.55
Number of Strands | 6
Outside Diamter of Cable Including Neutral (in) | 1.068
Diameter Under Neutral (Over Screen) (in) | 0.94
Outside Diamter of Cable Insulation (Under Screen) (in) | 0.86
Diameter of Conductor (in) | 0.362
Dielectric Constant of Insulation | 2.75
Construction Type | 1
Configuration 6: UG_1p_type2
Rmatrix (Ω/mile) | 1.6753
Xmatrix (Ω/mile) | 1.21
Cmatrix (nF/mile) | 207.8805
Size | 1/0
Material | AA
Current Carrying Capacity of Conductor (A) | 228
Phase Conductor Resistance (Ω/1000 ft) | 0.211
Geometric Mean Radisu of Phase Conductor (ft) | 0.111
Type Neutral | Concentric
Equivalent Resistance Concentric Neutral (Ω/1000 ft) | 0.55
Number of Strands | 6
Outside Diamter of Cable Including Neutral (in) | 1.068
Diameter Under Neutral (Over Screen) (in) | 0.94
Outside Diamter of Cable Insulation (Under Screen) (in) | 0.86
Diameter of Conductor (in) | 0.362
Dielectric Constant of Insulation | 2.75
Construction Type | 1
OH Neutral:#2/0 ACSR 6/1
Size | 2/0
Material | ACSR
Current Carrying Capacity (A) | 270
Resistance @ 25 °C (Ω/mile) | 0.706
Resistance @ 50 °C (Ω/mile) | 0.895
Geometric Mean Radisu (ft) | 0.0051
Conductor Diameter (in) | 0.447
OH Neutral:1 ACSR 6/1
Size | 1
Material | ACSR
Current Carrying Capacity (A) | 212
Resistance @ 25 °C (Ω/mile) | 1.1816
Resistance @ 50 °C (Ω/mile) | 1.2983
Geometric Mean Radisu (ft) | 0.011487
Conductor Diameter (in) | 0.354
Construction Type: 1 | GMDP (in) | GMDPN (in)
3 phase -OH | 58.6 | 53.6
V phase -OH | 88 | 55.8
Single phase - OH | 51 | 51
UG All phase | 5.4288 | 0
Construction Type: 2 | GMDP (in) | GMDPN (in)
3 phase -OH | 58.6 | 53.6
V phase -OH | 88 | 55.8
Single phase - OH | 51 | 51
UG All phase | 3 | 0

## Distribution Transformer
Three-phase Secondary Distribution Transformers (3Ø XFMR)
Name | Connection | Bus of Winding 1 | Bus of Winding 2 | Primary voltage rating (kV) | Secondary voltage rating (kV) | kVA rating (kVA) | %R | %X
T_1003 | Grd. Y - Grd. Y | bus1003 | T_bus1003_L | 13.8 | 0.208 | 112.5 | 2.43 | 3.87
T_1004 | Grd. Y - Grd. Y | bus1004 | T_bus1004_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_1005 | Grd. Y - Grd. Y | bus1005 | T_bus1005_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_1008 | Grd. Y - Grd. Y | bus1008 | T_bus1008_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_1009 | Grd. Y - Grd. Y | bus1009 | T_bus1009_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_1010 | Grd. Y - Grd. Y | bus1010 | T_bus1010_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_1013 | Grd. Y - Grd. Y | bus1013 | T_bus1013_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2002 | Grd. Y - Grd. Y | bus2002 | T_bus2002_L | 13.8 | 0.208 | 300 | 1.8 | 4.5
T_2003 | Grd. Y - Grd. Y | bus2003 | T_bus2003_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2005 | Grd. Y - Grd. Y | bus2005 | T_bus2005_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2010 | Grd. Y - Grd. Y | bus2010 | T_bus2010_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2011 | Grd. Y - Grd. Y | bus2011 | T_bus2011_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2029 | Grd. Y - Grd. Y | bus2029 | T_bus2029_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2030 | Grd. Y - Grd. Y | bus2030 | T_bus2030_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2032 | Grd. Y - Grd. Y | bus2032 | T_bus2032_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2034 | Grd. Y - Grd. Y | bus2034 | T_bus2034_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2035 | Grd. Y - Grd. Y | bus2035 | T_bus2035_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2037 | Grd. Y - Grd. Y | bus2037 | T_bus2037_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2040 | Grd. Y - Grd. Y | bus2040 | T_bus2040_L | 13.8 | 0.208 | 300 | 1.8 | 4.5
T_2041 | Grd. Y - Grd. Y | bus2041 | T_bus2041_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2042 | Grd. Y - Grd. Y | bus2042 | T_bus2042_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2043 | Grd. Y - Grd. Y | bus2043 | T_bus2043_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2052 | Grd. Y - Grd. Y | bus2052 | T_bus2052_L | 13.8 | 0.208 | 225 | 2.2 | 4.65
T_2053 | Grd. Y - Grd. Y | bus2053 | T_bus2053_L | 13.8 | 0.208 | 225 | 2.2 | 4.65
T_2058 | Grd. Y - Grd. Y | bus2058 | T_bus2058_L | 13.8 | 0.208 | 300 | 1.8 | 4.5
T_3002 | Grd. Y - Grd. Y | bus3002 | T_bus3002_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3004 | Grd. Y - Grd. Y | bus3004 | T_bus3004_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3006 | Grd. Y - Grd. Y | bus3006 | T_bus3006_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3007 | Grd. Y - Grd. Y | bus3007 | T_bus3007_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_3031 | Grd. Y - Grd. Y | bus3031 | T_bus3031_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3032 | Grd. Y - Grd. Y | bus3032 | T_bus3032_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3033 | Grd. Y - Grd. Y | bus3033 | T_bus3033_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3034 | Grd. Y - Grd. Y | bus3034 | T_bus3034_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3035 | Grd. Y - Grd. Y | bus3035 | T_bus3035_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3036 | Grd. Y - Grd. Y | bus3036 | T_bus3036_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3037 | Grd. Y - Grd. Y | bus3037 | T_bus3037_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3038 | Grd. Y - Grd. Y | bus3038 | T_bus3038_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3039 | Grd. Y - Grd. Y | bus3039 | T_bus3039_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3047 | Grd. Y - Grd. Y | bus3047 | T_bus3047_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3048 | Grd. Y - Grd. Y | bus3048 | T_bus3048_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3049 | Grd. Y - Grd. Y | bus3049 | T_bus3049_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3050 | Grd. Y - Grd. Y | bus3050 | T_bus3050_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3051 | Grd. Y - Grd. Y | bus3051 | T_bus3051_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3052 | Grd. Y - Grd. Y | bus3052 | T_bus3052_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3054 | Grd. Y - Grd. Y | bus3054 | T_bus3054_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3070 | Grd. Y - Grd. Y | bus3070 | T_bus3070_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3071 | Grd. Y - Grd. Y | bus3071 | T_bus3071_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3072 | Grd. Y - Grd. Y | bus3072 | T_bus3072_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3073 | Grd. Y - Grd. Y | bus3073 | T_bus3073_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3074 | Grd. Y - Grd. Y | bus3074 | T_bus3074_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3077 | Grd. Y - Grd. Y | bus3077 | T_bus3077_L | 13.8 | 0.208 | 500 | 1.6 | 5.9
T_3078 | Grd. Y - Grd. Y | bus3078 | T_bus3078_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3081 | Grd. Y - Grd. Y | bus3081 | T_bus3081_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
Single-phase Secondary Distribution Transformers (1Ø XFMR)
Name | Connection | Phases | Bus of Winding 1 | Bus of Winding 2 | Primary voltage rating (kV) | Secondary voltage rating (kV) | kVA rating (kVA) | %R | %X
T_1006 | Delta - Delta | AB | bus1006 | T_bus1006_L | 13.8 | 0.208 | 75 | 1 | 2.1
T_1007 | Delta - Delta | AB | bus1007 | T_bus1007_L | 13.8 | 0.208 | 25 | 1.33 | 1.88
Single-Phase Center-tapped Secondary Distribution Transformer (1Ø-CT XFMR)
Name | Bus of Winding 1 (Primary) | Phase of Winding 1 (Primary) | Voltage rating of Winding 1 (kV) | kVA rating of Winding 1 (kVA) | Bus of Winding 2 | Node of Winding 2 | Voltage rating of Winding 2 (kV) | kVA rating of Winding 2 (kVA) | Bus of Winding 3 | Node of Winding 3 | Voltage rating of Winding 3 (kV) | kVA rating of Winding 3 (kVA) | %R1 | %R2 | %R3 | %X12 | %X13 | %X23
T_1011 | bus1011 | A | 7.9677 | 25 | T_bus1011_L | 1 | 0.12 | 25 | T_bus1011_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_1012 | bus1012 | B | 7.9677 | 37.5 | T_bus1012_L | 1 | 0.12 | 37.5 | T_bus1012_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_1014 | bus1014 | B | 7.9677 | 25 | T_bus1014_L | 1 | 0.12 | 25 | T_bus1014_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_1015 | bus1015 | B | 7.9677 | 25 | T_bus1015_L | 1 | 0.12 | 25 | T_bus1015_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_1016 | bus1016 | C | 7.9677 | 50 | T_bus1016_L | 1 | 0.12 | 50 | T_bus1016_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_1017 | bus1017 | C | 7.9677 | 37.5 | T_bus1017_L | 1 | 0.12 | 37.5 | T_bus1017_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2008 | bus2008 | A | 7.9677 | 25 | T_bus2008_L | 1 | 0.12 | 25 | T_bus2008_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2009 | bus2009 | A | 7.9677 | 25 | T_bus2009_L | 1 | 0.12 | 25 | T_bus2009_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2014 | bus2014 | B | 7.9677 | 37.5 | T_bus2014_L | 1 | 0.12 | 37.5 | T_bus2014_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2015 | bus2015 | B | 7.9677 | 25 | T_bus2015_L | 1 | 0.12 | 25 | T_bus2015_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2016 | bus2016 | B | 7.9677 | 25 | T_bus2016_L | 1 | 0.12 | 25 | T_bus2016_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2017 | bus2017 | B | 7.9677 | 25 | T_bus2017_L | 1 | 0.12 | 25 | T_bus2017_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2018 | bus2018 | B | 7.9677 | 25 | T_bus2018_L | 1 | 0.12 | 25 | T_bus2018_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2020 | bus2020 | B | 7.9677 | 25 | T_bus2020_L | 1 | 0.12 | 25 | T_bus2020_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2022 | bus2022 | C | 7.9677 | 25 | T_bus2022_L | 1 | 0.12 | 25 | T_bus2022_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2023 | bus2023 | C | 7.9677 | 15 | T_bus2023_L | 1 | 0.12 | 15 | T_bus2023_L | 2 | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_2024 | bus2024 | C | 7.9677 | 25 | T_bus2024_L | 1 | 0.12 | 25 | T_bus2024_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2025 | bus2025 | C | 7.9677 | 25 | T_bus2025_L | 1 | 0.12 | 25 | T_bus2025_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2028 | bus2028 | A | 7.9677 | 25 | T_bus2028_L | 1 | 0.12 | 25 | T_bus2028_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2031 | bus2031 | A | 7.9677 | 25 | T_bus2031_L | 1 | 0.12 | 25 | T_bus2031_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2045 | bus2045 | B | 7.9677 | 15 | T_bus2045_L | 1 | 0.12 | 15 | T_bus2045_L | 2 | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_2046 | bus2046 | B | 7.9677 | 50 | T_bus2046_L | 1 | 0.12 | 50 | T_bus2046_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2047 | bus2047 | B | 7.9677 | 50 | T_bus2047_L | 1 | 0.12 | 50 | T_bus2047_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2048 | bus2048 | B | 7.9677 | 50 | T_bus2048_L | 1 | 0.12 | 50 | T_bus2048_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2049 | bus2049 | C | 7.9677 | 37.5 | T_bus2049_L | 1 | 0.12 | 37.5 | T_bus2049_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2050 | bus2050 | C | 7.9677 | 37.5 | T_bus2050_L | 1 | 0.12 | 37.5 | T_bus2050_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2051 | bus2051 | C | 7.9677 | 37.5 | T_bus2051_L | 1 | 0.12 | 37.5 | T_bus2051_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2054 | bus2054 | A | 7.9677 | 37.5 | T_bus2054_L | 1 | 0.12 | 37.5 | T_bus2054_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2055 | bus2055 | A | 7.9677 | 50 | T_bus2055_L | 1 | 0.12 | 50 | T_bus2055_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2056 | bus2056 | A | 7.9677 | 25 | T_bus2056_L | 1 | 0.12 | 25 | T_bus2056_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2059 | bus2059 | B | 7.9677 | 25 | T_bus2059_L | 1 | 0.12 | 25 | T_bus2059_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2060 | bus2060 | B | 7.9677 | 25 | T_bus2060_L | 1 | 0.12 | 25 | T_bus2060_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3009 | bus3009 | A | 7.9677 | 37.5 | T_bus3009_L | 1 | 0.12 | 37.5 | T_bus3009_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3010 | bus3010 | A | 7.9677 | 37.5 | T_bus3010_L | 1 | 0.12 | 37.5 | T_bus3010_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3011 | bus3011 | A | 7.9677 | 37.5 | T_bus3011_L | 1 | 0.12 | 37.5 | T_bus3011_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3012 | bus3012 | A | 7.9677 | 50 | T_bus3012_L | 1 | 0.12 | 50 | T_bus3012_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3013 | bus3013 | B | 7.9677 | 25 | T_bus3013_L | 1 | 0.12 | 25 | T_bus3013_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3014 | bus3014 | B | 7.9677 | 37.5 | T_bus3014_L | 1 | 0.12 | 37.5 | T_bus3014_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3016 | bus3016 | B | 7.9677 | 37.5 | T_bus3016_L | 1 | 0.12 | 37.5 | T_bus3016_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3017 | bus3017 | B | 7.9677 | 100 | T_bus3017_L | 1 | 0.12 | 100 | T_bus3017_L | 2 | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3018 | bus3018 | C | 7.9677 | 37.5 | T_bus3018_L | 1 | 0.12 | 37.5 | T_bus3018_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3019 | bus3019 | C | 7.9677 | 37.5 | T_bus3019_L | 1 | 0.12 | 37.5 | T_bus3019_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3020 | bus3020 | C | 7.9677 | 100 | T_bus3020_L | 1 | 0.12 | 100 | T_bus3020_L | 2 | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3021 | bus3021 | C | 7.9677 | 37.5 | T_bus3021_L | 1 | 0.12 | 37.5 | T_bus3021_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3023 | bus3023 | A | 7.9677 | 50 | T_bus3023_L | 1 | 0.12 | 50 | T_bus3023_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3024 | bus3024 | A | 7.9677 | 37.5 | T_bus3024_L | 1 | 0.12 | 37.5 | T_bus3024_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3025 | bus3025 | A | 7.9677 | 50 | T_bus3025_L | 1 | 0.12 | 50 | T_bus3025_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3026 | bus3026 | A | 7.9677 | 37.5 | T_bus3026_L | 1 | 0.12 | 37.5 | T_bus3026_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3027 | bus3027 | A | 7.9677 | 100 | T_bus3027_L | 1 | 0.12 | 100 | T_bus3027_L | 2 | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3028 | bus3028 | A | 7.9677 | 100 | T_bus3028_L | 1 | 0.12 | 100 | T_bus3028_L | 2 | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3029 | bus3029 | A | 7.9677 | 37.5 | T_bus3029_L | 1 | 0.12 | 37.5 | T_bus3029_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3041 | bus3041 | C | 7.9677 | 50 | T_bus3041_L | 1 | 0.12 | 50 | T_bus3041_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3042 | bus3042 | C | 7.9677 | 37.5 | T_bus3042_L | 1 | 0.12 | 37.5 | T_bus3042_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3043 | bus3043 | C | 7.9677 | 37.5 | T_bus3043_L | 1 | 0.12 | 37.5 | T_bus3043_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3044 | bus3044 | C | 7.9677 | 37.5 | T_bus3044_L | 1 | 0.12 | 37.5 | T_bus3044_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3045 | bus3045 | C | 7.9677 | 37.5 | T_bus3045_L | 1 | 0.12 | 37.5 | T_bus3045_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3056 | bus3056 | B | 7.9677 | 37.5 | T_bus3056_L | 1 | 0.12 | 37.5 | T_bus3056_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3057 | bus3057 | B | 7.9677 | 37.5 | T_bus3057_L | 1 | 0.12 | 37.5 | T_bus3057_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3058 | bus3058. | B | 7.9677 | 37.5 | T_bus3058_L | 1 | 0.12 | 37.5 | T_bus3058_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3059 | bus3059 | B | 7.9677 | 37.5 | T_bus3059_L | 1 | 0.12 | 37.5 | T_bus3059_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3060 | bus3060 | B | 7.9677 | 37.5 | T_bus3060_L | 1 | 0.12 | 37.5 | T_bus3060_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3061 | bus3061 | B | 7.9677 | 37.5 | T_bus3061_L | 1 | 0.12 | 37.5 | T_bus3061_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3062 | bus3062 | B | 7.9677 | 37.5 | T_bus3062_L | 1 | 0.12 | 37.5 | T_bus3062_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3063 | bus3063 | B | 7.9677 | 37.5 | T_bus3063_L | 1 | 0.12 | 37.5 | T_bus3063_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3064 | bus3064 | B | 7.9677 | 37.5 | T_bus3064_L | 1 | 0.12 | 37.5 | T_bus3064_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3065 | bus3065 | B | 7.9677 | 37.5 | T_bus3065_L | 1 | 0.12 | 37.5 | T_bus3065_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3066 | bus3066 | B | 7.9677 | 37.5 | T_bus3066_L | 1 | 0.12 | 37.5 | T_bus3066_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3067 | bus3067 | B | 7.9677 | 37.5 | T_bus3067_L | 1 | 0.12 | 37.5 | T_bus3067_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3083 | bus3083 | A | 7.9677 | 37.5 | T_bus3083_L | 1 | 0.12 | 37.5 | T_bus3083_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3084 | bus3084 | A | 7.9677 | 37.5 | T_bus3084_L | 1 | 0.12 | 37.5 | T_bus3084_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3085 | bus3085 | A | 7.9677 | 37.5 | T_bus3085_L | 1 | 0.12 | 37.5 | T_bus3085_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3086 | bus3086 | A | 7.9677 | 37.5 | T_bus3086_L | 1 | 0.12 | 37.5 | T_bus3086_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3087 | bus3087 | A | 7.9677 | 37.5 | T_bus3087_L | 1 | 0.12 | 37.5 | T_bus3087_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3088 | bus3088 | A | 7.9677 | 37.5 | T_bus3088_L | 1 | 0.12 | 37.5 | T_bus3088_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3089 | bus3089 | A | 7.9677 | 37.5 | T_bus3089_L | 1 | 0.12 | 37.5 | T_bus3089_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3090 | bus3090 | A | 7.9677 | 37.5 | T_bus3090_L | 1 | 0.12 | 37.5 | T_bus3090_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3091 | bus3091 | A | 7.9677 | 25 | T_bus3091_L | 1 | 0.12 | 25 | T_bus3091_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3093 | bus3093 | A | 7.9677 | 37.5 | T_bus3093_L | 1 | 0.12 | 37.5 | T_bus3093_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3094 | bus3094 | A | 7.9677 | 37.5 | T_bus3094_L | 1 | 0.12 | 37.5 | T_bus3094_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3095 | bus3095 | A | 7.9677 | 37.5 | T_bus3095_L | 1 | 0.12 | 37.5 | T_bus3095_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3096 | bus3096 | A | 7.9677 | 37.5 | T_bus3096_L | 1 | 0.12 | 37.5 | T_bus3096_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3097 | bus3097 | A | 7.9677 | 37.5 | T_bus3097_L | 1 | 0.12 | 37.5 | T_bus3097_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3098 | bus3098 | B | 7.9677 | 50 | T_bus3098_L | 1 | 0.12 | 50 | T_bus3098_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3099 | bus3099 | B | 7.9677 | 37.5 | T_bus3099_L | 1 | 0.12 | 37.5 | T_bus3099_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3101 | bus3101 | C | 7.9677 | 37.5 | T_bus3101_L | 1 | 0.12 | 37.5 | T_bus3101_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3102 | bus3102 | C | 7.9677 | 37.5 | T_bus3102_L | 1 | 0.12 | 37.5 | T_bus3102_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3103 | bus3103 | C | 7.9677 | 50 | T_bus3103_L | 1 | 0.12 | 50 | T_bus3103_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3104 | bus3104 | C | 7.9677 | 100 | T_bus3104_L | 1 | 0.12 | 100 | T_bus3104_L | 2 | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3105 | bus3105 | C | 7.9677 | 37.5 | T_bus3105_L | 1 | 0.12 | 37.5 | T_bus3105_L. | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3106 | bus3106 | C | 7.9677 | 100 | T_bus3106_L | 1 | 0.12 | 100 | T_bus3106_L | 2 | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3108 | bus3108 | A | 7.9677 | 37.5 | T_bus3108_L | 1 | 0.12 | 37.5 | T_bus3108_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3109 | bus3109 | A | 7.9677 | 37.5 | T_bus3109_L | 1 | 0.12 | 37.5 | T_bus3109_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3110 | bus3110 | A | 7.9677 | 50 | T_bus3110_L | 1 | 0.12 | 50 | T_bus3110_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3111 | bus3111 | A | 7.9677 | 50 | T_bus3111_L | 1 | 0.12 | 50 | T_bus3111_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3112 | bus3112 | A | 7.9677 | 50 | T_bus3112_L | 1 | 0.12 | 50 | T_bus3112_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3114 | bus3114 | B | 7.9677 | 37.5 | T_bus3114_L | 1 | 0.12 | 37.5 | T_bus3114_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3115 | bus3115 | B | 7.9677 | 50 | T_bus3115_L | 1 | 0.12 | 50 | T_bus3115_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3116 | bus3116 | B | 7.9677 | 37.5 | T_bus3116_L | 1 | 0.12 | 37.5 | T_bus3116_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3117 | bus3117 | B | 7.9677 | 37.5 | T_bus3117_L | 1 | 0.12 | 37.5 | T_bus3117_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3120 | bus3120 | B | 7.9677 | 37.5 | T_bus3120_L | 1 | 0.12 | 37.5 | T_bus3120_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3121 | bus3121 | B | 7.9677 | 37.5 | T_bus3121_L | 1 | 0.12 | 37.5 | T_bus3121_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3122 | bus3122 | B | 7.9677 | 37.5 | T_bus3122_L | 1 | 0.12 | 37.5 | T_bus3122_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3123 | bus3123 | B | 7.9677 | 37.5 | T_bus3123_L | 1 | 0.12 | 37.5 | T_bus3123_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3124 | bus3124 | B | 7.9677 | 37.5 | T_bus3124_L | 1 | 0.12 | 37.5 | T_bus3124_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3125 | bus3125 | B | 7.9677 | 15 | T_bus3125_L | 1 | 0.12 | 15 | T_bus3125_L | 2 | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_3126 | bus3126 | B | 7.9677 | 37.5 | T_bus3126_L | 1 | 0.12 | 37.5 | T_bus3126_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3127 | bus3127 | B | 7.9677 | 37.5 | T_bus3127_L | 1 | 0.12 | 37.5 | T_bus3127_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3128 | bus3128 | B | 7.9677 | 37.5 | T_bus3128_L | 1 | 0.12 | 37.5 | T_bus3128_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3129 | bus3129 | B | 7.9677 | 37.5 | T_bus3129_L | 1 | 0.12 | 37.5 | T_bus3129_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3130 | bus3130 | B | 7.9677 | 37.5 | T_bus3130_L | 1 | 0.12 | 37.5 | T_bus3130_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3131 | bus3131 | B | 7.9677 | 37.5 | T_bus3131_L | 1 | 0.12 | 37.5 | T_bus3131_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3132 | bus3132 | A | 7.9677 | 50 | T_bus3132_L | 1 | 0.12 | 50 | T_bus3132_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3134 | bus3134 | A | 7.9677 | 50 | T_bus3134_L | 1 | 0.12 | 50 | T_bus3134_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3135 | bus3135 | A | 7.9677 | 37.5 | T_bus3135_L | 1 | 0.12 | 37.5 | T_bus3135_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3136 | bus3136 | A | 7.9677 | 50 | T_bus3136_L | 1 | 0.12 | 50 | T_bus3136_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3137 | bus3137 | A | 7.9677 | 50 | T_bus3137_L | 1 | 0.12 | 50 | T_bus3137_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3138 | bus3138 | A | 7.9677 | 50 | T_bus3138_L | 1 | 0.12 | 50 | T_bus3138_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3139 | bus3139 | A | 7.9677 | 37.5 | T_bus3139_L | 1 | 0.12 | 37.5 | T_bus3139_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3141 | bus3141 | C | 7.9677 | 37.5 | T_bus3141_L | 1 | 0.12 | 37.5 | T_bus3141_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3142 | bus3142 | C | 7.9677 | 37.5 | T_bus3142_L | 1 | 0.12 | 37.5 | T_bus3142_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3143 | bus3143 | C | 7.9677 | 37.5 | T_bus3143_L | 1 | 0.12 | 37.5 | T_bus3143_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3144 | bus3144 | C | 7.9677 | 15 | T_bus3144_L | 1 | 0.12 | 15 | T_bus3144_L | 2 | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_3145 | bus3145 | C | 7.9677 | 37.5 | T_bus3145_L | 1 | 0.12 | 37.5 | T_bus3145_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3146 | bus3146 | C | 7.9677 | 37.5 | T_bus3146_L | 1 | 0.12 | 37.5 | T_bus3146_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3147 | bus3147 | C | 7.9677 | 37.5 | T_bus3147_L | 1 | 0.12 | 37.5 | T_bus3147_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3148 | bus3148 | C | 7.9677 | 50 | T_bus3148_L | 1 | 0.12 | 50 | T_bus3148_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3149 | bus3149 | C | 7.9677 | 37.5 | T_bus3149_L | 1 | 0.12 | 37.5 | T_bus3149_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3150 | bus3150 | C | 7.9677 | 25 | T_bus3150_L | 1 | 0.12 | 25 | T_bus3150_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3151 | bus3151 | C | 7.9677 | 25 | T_bus3151_L | 1 | 0.12 | 25 | T_bus3151_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3152 | bus3152 | C | 7.9677 | 25 | T_bus3152_L | 1 | 0.12 | 25 | T_bus3152_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3153 | bus3153 | C | 7.9677 | 37.5 | T_bus3153_L | 1 | 0.12 | 37.5 | T_bus3153_L | 2 | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3154 | bus3154 | C | 7.9677 | 25 | T_bus3154_L | 1 | 0.12 | 25 | T_bus3154_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3155 | bus3155 | C | 7.9677 | 25 | T_bus3155_L | 1 | 0.12 | 25 | T_bus3155_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3157 | bus3157 | C | 7.9677 | 50 | T_bus3157_L | 1 | 0.12 | 50 | T_bus3157_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3158 | bus3158 | C | 7.9677 | 50 | T_bus3158_L | 1 | 0.12 | 50 | T_bus3158_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3159 | bus3159 | C | 7.9677 | 50 | T_bus3159_L | 1 | 0.12 | 50 | T_bus3159_L | 2 | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3160 | bus3160 | C | 7.9677 | 25 | T_bus3160_L | 1 | 0.12 | 25 | T_bus3160_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3161 | bus3161 | C | 7.9677 | 25 | T_bus3161_L | 1 | 0.12 | 25 | T_bus3161_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3162 | bus3162 | C | 7.9677 | 25 | T_bus3162_L | 1 | 0.12 | 25 | T_bus3162_L | 2 | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
Note: The impedance parameters of single-phase center-tapped transformers are calculated using equation (1) in [1]. [1] W. H. Kersting, “Center-Tapped Transformer and 120-/240-V Secondary Models,” IEEE Trans. Ind. Appl., vol. 45, pp. 575–581, Mar./Apr. 2009.

## Circuit Breakers
Three-Phase Circuit Breakers
Name | Bus A | Bus B | Positive‐sequence resistance (Ω/foot) | Zero-sequence resistance (Ω/foot) | Positive‐sequence reactance (Ω/foot) | Zero-sequence reactance (Ω/foot) | Positive‐sequence capacitance (nF/foot) | Zero‐sequence capacitance (nF/foot) | Normal Status
CB_101 | bus1 | bus1001 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_102 | bus1010 | bus2057 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Open
CB_201 | bus1 | bus2001 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_202 | bus2012 | bus2013 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_203 | bus2021 | bus2026 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_204 | bus2013 | bus3005 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Open
CB_301 | bus1 | bus3001 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_302 | bus3075 | bus3076 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_303 | bus3081 | bus2016 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Open

## Capacitor Banks
Three-Phase Shunt Capacitor Bank
Name | Bus | kV Rating (kV) | Connection | kVAr rating (kVAr) | Normal Status
CAP_201 | bus2038 | 13.8 | wye - Grd. | 50 | Closed
CAP_301 | bus3079 | 13.8 | wye - Grd. | 50 | Closed

## Load Configuration
Note: For the loads connected to single-phase center-tapped transformers: 1. The loads are defined as two 120V loads connected line to neutral. 2. kW load is divided equally between the two "Nodes". 3. For phases>1, OpenDSS Load model assumes that a 2-phase load is 2 phases of a 3-phase system and requires the voltage base to be specified same as 3-phase (Line-Line kV = Line-Neutral * sqrt(3)). Thus, the base voltage is 208V to get 120V line-to-neutral. 4. For the three-phase load, Voltage is specified as the rated line-to-line voltage (208V). For the single-phase load, Voltage is specified as the rated line-to-neutral voltage (120V).
Three-phase transformer and three-phase load connection
Transformer type definition: Three-phase transformer: 3Ø XFMR Single-phase transformer: 1Ø XFMR Single-phase center-tapped transformer: 1Ø-CT XFMR
Spot Loads Configuration
Load Name | XFMR Type | Bus | Voltage (V) | Connection & Load Model | Number of customers
Load_1003 | 3Ø XFMR | T_bus1003_L | 208 | wye-PQ | 4
Load_1004 | 3Ø XFMR | T_bus1004_L | 208 | wye-PQ | 2
Load_1005 | 3Ø XFMR | T_bus1005_L | 208 | wye-PQ | 2
Load_1006 | 1Ø XFMR | T_b6us1006_L | 208 | delta-PQ | 2
Load_1007 | 1Ø XFMR | T_bu7s1007_L | 208 | delta-PQ | 2
Load_1008 | 3Ø XFMR | T_bus1008_L | 208 | wye-PQ | 3
Load_1009 | 3Ø XFMR | T_bus1009_L | 208 | wye-PQ | 2
Load_1010 | 3Ø XFMR | T_bus1010_L | 208 | wye-PQ | 4 |  | Single-phase center-tapped transformer and single-phase load connection
Load_1011 | 1Ø-CT XFMR | T_bus1011_L | 120 | wye-PQ | 13
Load_1012 | 1Ø-CT XFMR | T_bus1012_L | 120 | wye-PQ | 7
Load_1013 | 3Ø XFMR | T_bus1013_L | 208 | wye-PQ | 3
Load_1014 | 1Ø-CT XFMR | T_bus1014_L | 120 | wye-PQ | 2
Load_1015 | 1Ø-CT XFMR | T_bus1015_L | 120 | wye-PQ | 3
Load_1016 | 1Ø-CT XFMR | T_bus1016_L | 120 | wye-PQ | 7
Load_1017 | 1Ø-CT XFMR | T_bus1017_L | 120 | wye-PQ | 7
Load_2002 | 3Ø XFMR | T_bus2002_L | 208 | wye-PQ | 4
Load_2003 | 3Ø XFMR | T_bus2003_L | 208 | wye-PQ | 3
Load_2005 | 3Ø XFMR | T_bus2005_L | 208 | wye-PQ | 2
Load_2008 | 1Ø-CT XFMR | T_bus2008_L | 120 | wye-PQ | 4
Load_2009 | 1Ø-CT XFMR | T_bus2009_L | 120 | wye-PQ | 2
Load_2010 | 3Ø XFMR | T_bus2010_L | 208 | wye-PQ | 5
Load_2011 | 3Ø XFMR | T_bus2011_L | 208 | wye-PQ | 7
Load_2014 | 1Ø-CT XFMR | T_bus2014_L | 120 | wye-PQ | 4
Load_2015 | 1Ø-CT XFMR | T_bus2015_L | 120 | wye-PQ | 2
Load_2016 | 1Ø-CT XFMR | T_bus2016_L | 120 | wye-PQ | 3
Load_2017 | 1Ø-CT XFMR | T_bus2017_L | 120 | wye-PQ | 6
Load_2018 | 1Ø-CT XFMR | T_bus2018_L | 120 | wye-PQ | 4
Load_2020 | 1Ø-CT XFMR | T_bus2020_L | 120 | wye-PQ | 2
Load_2022 | 1Ø-CT XFMR | T_bus2022_L | 120 | wye-PQ | 3
Load_2023 | 1Ø-CT XFMR | T_bus2023_L | 120 | wye-PQ | 2
Load_2024 | 1Ø-CT XFMR | T_bus2024_L | 120 | wye-PQ | 4
Load_2025 | 1Ø-CT XFMR | T_bus2025_L | 120 | wye-PQ | 4
Load_2028 | 1Ø-CT XFMR | T_bus2028_L | 120 | wye-PQ | 1
Load_2029 | 3Ø XFMR | T_bus2029_L | 208 | wye-PQ | 2
Load_2030 | 3Ø XFMR | T_bus2030_L | 208 | wye-PQ | 3
Load_2031 | 1Ø-CT XFMR | T_bus2031_L | 120 | wye-PQ | 3
Load_2032 | 3Ø XFMR | T_bus2032_L | 208 | wye-PQ | 4
Load_2034 | 3Ø XFMR | T_bus2034_L | 208 | wye-PQ | 5
Load_2035 | 3Ø XFMR | T_bus2035_L | 208 | wye-PQ | 3
Load_2037 | 3Ø XFMR | T_bus2037_L | 208 | wye-PQ | 4
Load_2040 | 3Ø XFMR | T_bus2040_L | 208 | wye-PQ | 4
Load_2041 | 3Ø XFMR | T_bus2041_L | 208 | wye-PQ | 2
Load_2042 | 3Ø XFMR | T_bus2042_L | 208 | wye-PQ | 2
Load_2043 | 3Ø XFMR | T_bus2043_L | 208 | wye-PQ | 6
Load_2045 | 1Ø-CT XFMR | T_bus2045_L | 120 | wye-PQ | 2
Load_2046 | 1Ø-CT XFMR | T_bus2046_L | 120 | wye-PQ | 8
Load_2047 | 1Ø-CT XFMR | T_bus2047_L | 120 | wye-PQ | 8
Load_2048 | 1Ø-CT XFMR | T_bus2048_L | 120 | wye-PQ | 7
Load_2049 | 1Ø-CT XFMR | T_bus2049_L | 120 | wye-PQ | 4
Load_2050 | 1Ø-CT XFMR | T_bus2050_L | 120 | wye-PQ | 3
Load_2051 | 1Ø-CT XFMR | T_bus2051_L | 120 | wye-PQ | 6
Load_2052 | 3Ø XFMR | T_bus2052_L | 208 | wye-PQ | 3
Load_2053 | 3Ø XFMR | T_bus2053_L | 208 | wye-PQ | 1
Load_2054 | 1Ø-CT XFMR | T_bus2054_L | 120 | wye-PQ | 8
Load_2055 | 1Ø-CT XFMR | T_bus2055_L | 120 | wye-PQ | 7
Load_2056 | 1Ø-CT XFMR | T_bus2056_L | 120 | wye-PQ | 4
Load_2058 | 3Ø XFMR | T_bus2058_L | 208 | wye-PQ | 4
Load_2059 | 1Ø-CT XFMR | T_bus2059_L | 120 | wye-PQ | 2
Load_2060 | 1Ø-CT XFMR | T_bus2060_L | 120 | wye-PQ | 2
Load_3002 | 3Ø XFMR | T_bus3002_L | 208 | wye-PQ | 5
Load_3004 | 3Ø XFMR | T_bus3004_L | 208 | wye-PQ | 4
Load_3006 | 3Ø XFMR | T_bus3006_L | 208 | wye-PQ | 6
Load_3007 | 3Ø XFMR | T_bus3007_L | 208 | wye-PQ | 8
Load_3009 | 1Ø-CT XFMR | T_bus3009_L | 120 | wye-PQ | 7
Load_3010 | 1Ø-CT XFMR | T_bus3010_L | 120 | wye-PQ | 8
Load_3011 | 1Ø-CT XFMR | T_bus3011_L | 120 | wye-PQ | 7
Load_3012 | 1Ø-CT XFMR | T_bus3012_L | 120 | wye-PQ | 9
Load_3013 | 1Ø-CT XFMR | T_bus3013_L | 120 | wye-PQ | 5
Load_3014 | 1Ø-CT XFMR | T_bus3014_L | 120 | wye-PQ | 7
Load_3016 | 1Ø-CT XFMR | T_bus3016_L | 120 | wye-PQ | 9
Load_3017 | 1Ø-CT XFMR | T_bus3017_L | 120 | wye-PQ | 12
Load_3018 | 1Ø-CT XFMR | T_bus3018_L | 120 | wye-PQ | 11
Load_3019 | 1Ø-CT XFMR | T_bus3019_L | 120 | wye-PQ | 9
Load_3020 | 1Ø-CT XFMR | T_bus3020_L | 120 | wye-PQ | 9
Load_3021 | 1Ø-CT XFMR | T_bus3021_L | 120 | wye-PQ | 7
Load_3023 | 1Ø-CT XFMR | T_bus3023_L | 120 | wye-PQ | 9
Load_3024 | 1Ø-CT XFMR | T_bus3024_L | 120 | wye-PQ | 9
Load_3025 | 1Ø-CT XFMR | T_bus3025_L | 120 | wye-PQ | 9
Load_3026 | 1Ø-CT XFMR | T_bus3026_L | 120 | wye-PQ | 9
Load_3027 | 1Ø-CT XFMR | T_bus3027_L | 120 | wye-PQ | 12
Load_3028 | 1Ø-CT XFMR | T_bus3028_L | 120 | wye-PQ | 8
Load_3029 | 1Ø-CT XFMR | T_bus3029_L | 120 | wye-PQ | 5
Load_3031 | 3Ø XFMR | T_bus3031_L | 208 | wye-PQ | 8
Load_3032 | 3Ø XFMR | T_bus3032_L | 208 | wye-PQ | 9
Load_3033 | 3Ø XFMR | T_bus3033_L | 208 | wye-PQ | 7
Load_3034 | 3Ø XFMR | T_bus3034_L | 208 | wye-PQ | 9
Load_3035 | 3Ø XFMR | T_bus3035_L | 208 | wye-PQ | 8
Load_3036 | 3Ø XFMR | T_bus3036_L | 208 | wye-PQ | 5
Load_3037 | 3Ø XFMR | T_bus3037_L | 208 | wye-PQ | 7
Load_3038 | 3Ø XFMR | T_bus3038_L | 208 | wye-PQ | 7
Load_3039 | 3Ø XFMR | T_bus3039_L | 208 | wye-PQ | 6
Load_3041 | 1Ø-CT XFMR | T_bus3041_L | 120 | wye-PQ | 9
Load_3042 | 1Ø-CT XFMR | T_bus3042_L | 120 | wye-PQ | 8
Load_3043 | 1Ø-CT XFMR | T_bus3043_L | 120 | wye-PQ | 7
Load_3044 | 1Ø-CT XFMR | T_bus3044_L | 120 | wye-PQ | 9
Load_3045 | 1Ø-CT XFMR | T_bus3045_L | 120 | wye-PQ | 6
Load_3047 | 3Ø XFMR | T_bus3047_L | 208 | wye-PQ | 6
Load_3048 | 3Ø XFMR | T_bus3048_L | 208 | wye-PQ | 3
Load_3049 | 3Ø XFMR | T_bus3049_L | 208 | wye-PQ | 5
Load_3050 | 3Ø XFMR | T_bus3050_L | 208 | wye-PQ | 6
Load_3051 | 3Ø XFMR | T_bus3051_L | 208 | wye-PQ | 4
Load_3052 | 3Ø XFMR | T_bus3052_L | 208 | wye-PQ | 5
Load_3054 | 3Ø XFMR | T_bus3054_L | 208 | wye-PQ | 2
Load_3056 | 1Ø-CT XFMR | T_bus3056_L | 120 | wye-PQ | 4
Load_3057 | 1Ø-CT XFMR | T_bus3057_L | 120 | wye-PQ | 4
Load_3058 | 1Ø-CT XFMR | T_bus3058_L | 120 | wye-PQ | 5
Load_3059 | 1Ø-CT XFMR | T_bus3059_L | 120 | wye-PQ | 3
Load_3060 | 1Ø-CT XFMR | T_bus3060_L | 120 | wye-PQ | 4
Load_3061 | 1Ø-CT XFMR | T_bus3061_L | 120 | wye-PQ | 4
Load_3062 | 1Ø-CT XFMR | T_bus3062_L | 120 | wye-PQ | 3
Load_3063 | 1Ø-CT XFMR | T_bus3063_L | 120 | wye-PQ | 4
Load_3064 | 1Ø-CT XFMR | T_bus3064_L | 120 | wye-PQ | 6
Load_3065 | 1Ø-CT XFMR | T_bus3065_L | 120 | wye-PQ | 7
Load_3066 | 1Ø-CT XFMR | T_bus3066_L | 120 | wye-PQ | 3
Load_3067 | 1Ø-CT XFMR | T_bus3067_L | 120 | wye-PQ | 8
Load_3070 | 3Ø XFMR | T_bus3070_L | 208 | wye-PQ | 5
Load_3071 | 3Ø XFMR | T_bus3071_L | 208 | wye-PQ | 9
Load_3072 | 3Ø XFMR | T_bus3072_L | 208 | wye-PQ | 7
Load_3073 | 3Ø XFMR | T_bus3073_L | 208 | wye-PQ | 4
Load_3074 | 3Ø XFMR | T_bus3074_L | 208 | wye-PQ | 4
Load_3077 | 3Ø XFMR | T_bus3077_L | 208 | wye-PQ | 4
Load_3078 | 3Ø XFMR | T_bus3078_L | 208 | wye-PQ | 5
Load_3081 | 3Ø XFMR | T_bus3081_L | 208 | wye-PQ | 2
Load_3083 | 1Ø-CT XFMR | T_bus3083_L | 120 | wye-PQ | 10
Load_3084 | 1Ø-CT XFMR | T_bus3084_L | 120 | wye-PQ | 3
Load_3085 | 1Ø-CT XFMR | T_bus3085_L | 120 | wye-PQ | 8
Load_3086 | 1Ø-CT XFMR | T_bus3086_L | 120 | wye-PQ | 5
Load_3087 | 1Ø-CT XFMR | T_bus3087_L | 120 | wye-PQ | 6
Load_3088 | 1Ø-CT XFMR | T_bus3088_L | 120 | wye-PQ | 7
Load_3089 | 1Ø-CT XFMR | T_bus3089_L | 120 | wye-PQ | 3
Load_3090 | 1Ø-CT XFMR | T_bus3090_L | 120 | wye-PQ | 7
Load_3091 | 1Ø-CT XFMR | T_bus3091_L | 120 | wye-PQ | 3
Load_3093 | 1Ø-CT XFMR | T_bus3093_L | 120 | wye-PQ | 10
Load_3094 | 1Ø-CT XFMR | T_bus3094_L | 120 | wye-PQ | 9
Load_3095 | 1Ø-CT XFMR | T_bus3095_L | 120 | wye-PQ | 11
Load_3096 | 1Ø-CT XFMR | T_bus3096_L | 120 | wye-PQ | 11
Load_3097 | 1Ø-CT XFMR | T_bus3097_L | 120 | wye-PQ | 5
Load_3098 | 1Ø-CT XFMR | T_bus3098_L | 120 | wye-PQ | 9
Load_3099 | 1Ø-CT XFMR | T_bus3099_L | 120 | wye-PQ | 7
Load_3101 | 1Ø-CT XFMR | T_bus3101_L | 120 | wye-PQ | 3
Load_3102 | 1Ø-CT XFMR | T_bus3102_L | 120 | wye-PQ | 5
Load_3103 | 1Ø-CT XFMR | T_bus3103_L | 120 | wye-PQ | 9
Load_3104 | 1Ø-CT XFMR | T_bus3104_L | 120 | wye-PQ | 2
Load_3105 | 1Ø-CT XFMR | T_bus3105_L | 120 | wye-PQ | 5
Load_3106 | 1Ø-CT XFMR | T_bus3106_L | 120 | wye-PQ | 9
Load_3108 | 1Ø-CT XFMR | T_bus3108_L | 120 | wye-PQ | 4
Load_3109 | 1Ø-CT XFMR | T_bus3109_L | 120 | wye-PQ | 5
Load_3110 | 1Ø-CT XFMR | T_bus3110_L | 120 | wye-PQ | 10
Load_3111 | 1Ø-CT XFMR | T_bus3111_L | 120 | wye-PQ | 11
Load_3112 | 1Ø-CT XFMR | T_bus3112_L | 120 | wye-PQ | 5
Load_3114 | 1Ø-CT XFMR | T_bus3114_L | 120 | wye-PQ | 9
Load_3115 | 1Ø-CT XFMR | T_bus3115_L | 120 | wye-PQ | 8
Load_3116 | 1Ø-CT XFMR | T_bus3116_L | 120 | wye-PQ | 8
Load_3117 | 1Ø-CT XFMR | T_bus3117_L | 120 | wye-PQ | 4
Load_3120 | 1Ø-CT XFMR | T_bus3120_L | 120 | wye-PQ | 3
Load_3121 | 1Ø-CT XFMR | T_bus3121_L | 120 | wye-PQ | 6
Load_3122 | 1Ø-CT XFMR | T_bus3122_L | 120 | wye-PQ | 3
Load_3123 | 1Ø-CT XFMR | T_bus3123_L | 120 | wye-PQ | 6
Load_3124 | 1Ø-CT XFMR | T_bus3124_L | 120 | wye-PQ | 3
Load_3125 | 1Ø-CT XFMR | T_bus3125_L | 120 | wye-PQ | 2
Load_3126 | 1Ø-CT XFMR | T_bus3126_L | 120 | wye-PQ | 5
Load_3127 | 1Ø-CT XFMR | T_bus3127_L | 120 | wye-PQ | 8
Load_3128 | 1Ø-CT XFMR | T_bus3128_L | 120 | wye-PQ | 4
Load_3129 | 1Ø-CT XFMR | T_bus3129_L | 120 | wye-PQ | 3
Load_3130 | 1Ø-CT XFMR | T_bus3130_L | 120 | wye-PQ | 5
Load_3131 | 1Ø-CT XFMR | T_bus3131_L | 120 | wye-PQ | 7
Load_3132 | 1Ø-CT XFMR | T_bus3132_L | 120 | wye-PQ | 5
Load_3134 | 1Ø-CT XFMR | T_bus3134_L | 120 | wye-PQ | 6
Load_3135 | 1Ø-CT XFMR | T_bus3135_L | 120 | wye-PQ | 6
Load_3136 | 1Ø-CT XFMR | T_bus3136_L | 120 | wye-PQ | 7
Load_3137 | 1Ø-CT XFMR | T_bus3137_L | 120 | wye-PQ | 9
Load_3138 | 1Ø-CT XFMR | T_bus3138_L | 120 | wye-PQ | 5
Load_3139 | 1Ø-CT XFMR | T_bus3139_L | 120 | wye-PQ | 1
Load_3141 | 1Ø-CT XFMR | T_bus3141_L | 120 | wye-PQ | 5
Load_3142 | 1Ø-CT XFMR | T_bus3142_L | 120 | wye-PQ | 5
Load_3143 | 1Ø-CT XFMR | T_bus3143_L | 120 | wye-PQ | 7
Load_3144 | 1Ø-CT XFMR | T_bus3144_L | 120 | wye-PQ | 3
Load_3145 | 1Ø-CT XFMR | T_bus3145_L | 120 | wye-PQ | 5
Load_3146 | 1Ø-CT XFMR | T_bus3146_L | 120 | wye-PQ | 5
Load_3147 | 1Ø-CT XFMR | T_bus3147_L | 120 | wye-PQ | 17
Load_3148 | 1Ø-CT XFMR | T_bus3148_L | 120 | wye-PQ | 8
Load_3149 | 1Ø-CT XFMR | T_bus3149_L | 120 | wye-PQ | 4
Load_3150 | 1Ø-CT XFMR | T_bus3150_L | 120 | wye-PQ | 4
Load_3151 | 1Ø-CT XFMR | T_bus3151_L | 120 | wye-PQ | 4
Load_3152 | 1Ø-CT XFMR | T_bus3152_L | 120 | wye-PQ | 3
Load_3153 | 1Ø-CT XFMR | T_bus3153_L | 120 | wye-PQ | 8
Load_3154 | 1Ø-CT XFMR | T_bus3154_L | 120 | wye-PQ | 4
Load_3155 | 1Ø-CT XFMR | T_bus3155_L | 120 | wye-PQ | 4
Load_3157 | 1Ø-CT XFMR | T_bus3157_L | 120 | wye-PQ | 12
Load_3158 | 1Ø-CT XFMR | T_bus3158_L | 120 | wye-PQ | 7
Load_3159 | 1Ø-CT XFMR | T_bus3159_L | 120 | wye-PQ | 10
Load_3160 | 1Ø-CT XFMR | T_bus3160_L | 120 | wye-PQ | 4
Load_3161 | 1Ø-CT XFMR | T_bus3161_L | 120 | wye-PQ | 5
Load_3162 | 1Ø-CT XFMR | T_bus3162_L | 120 | wye-PQ | 3

## Bus Coordinates
Bus Name | X | Y
bus1 | 10.52 | 13.6
bus1001 | 10.19 | 13.04
bus1002 | 8.9 | 14.11
bus1003 | 8.9 | 13.36
bus1004 | 7.77 | 14.11
bus1005 | 6.4 | 14.11
bus1006 | 5.15 | 14.11
bus1007 | 5.15 | 12.98
bus1008 | 3.71 | 14.11
bus1009 | 2.4 | 14.11
bus1010 | 1.4 | 14.11
bus1011 | 2.4 | 12.98
bus1012 | 2.4 | 12.11
bus1013 | 2.4 | 11.23
bus1014 | 3.85 | 11.23
bus1015 | 4.85 | 11.23
bus1016 | 2.4 | 10.48
bus1017 | 2.4 | 9.73
bus2001 | 10.52 | 12.23
bus2002 | 9.56 | 7.58
bus2003 | 8.3 | 7.58
bus2004 | 7.07 | 7.58
bus2005 | 5.77 | 7.58
bus2006 | 4.54 | 7.58
bus2007 | 4.55 | 8.25
bus2008 | 3.66 | 8.25
bus2009 | 4.55 | 8.93
bus2010 | 3.68 | 7.58
bus2011 | 2.71 | 7.58
bus2012 | 2.32 | 7.1
bus2013 | 2.31 | 6.44
bus2014 | 2.31 | 5.68
bus2015 | 1.41 | 5.68
bus2016 | 2.31 | 4.97
bus2017 | 2.31 | 4.24
bus2018 | 2.31 | 3.51
bus2019 | 3.23 | 6.45
bus2020 | 3.23 | 5.85
bus2021 | 4.04 | 6.44
bus2022 | 4.04 | 5.72
bus2023 | 4.04 | 4.99
bus2024 | 4.04 | 4.26
bus2025 | 4.04 | 3.53
bus2026 | 4.8 | 6.45
bus2027 | 5.59 | 6.45
bus2028 | 5.59 | 5.88
bus2029 | 5.58 | 5.31
bus2030 | 5.58 | 4.73
bus2031 | 5.58 | 4.16
bus2032 | 6.61 | 6.45
bus2033 | 7.6 | 6.45
bus2034 | 7.6 | 5.79
bus2035 | 8.46 | 6.44
bus2036 | 9.3 | 6.45
bus2037 | 10.21 | 6.45
bus2038 | 10.21 | 5.84
bus2039 | 10.21 | 4.98
bus2040 | 11.07 | 4.98
bus2041 | 11.88 | 4.98
bus2042 | 10.21 | 4.39
bus2043 | 10.21 | 3.63
bus2044 | 8.76 | 3.63
bus2045 | 8.76 | 4.29
bus2046 | 8.76 | 5
bus2047 | 7.84 | 4.29
bus2048 | 6.92 | 4.29
bus2049 | 7.87 | 3.63
bus2050 | 7.01 | 3.63
bus2051 | 6.16 | 3.62
bus2052 | 6.16 | 2.81
bus2053 | 8.76 | 2.1
bus2054 | 7.78 | 2.1
bus2055 | 6.84 | 2.1
bus2056 | 5.86 | 2.1
bus2057 | 8.76 | 1.4
bus2058 | 9.9 | 1.4
bus2059 | 7.72 | 1.4
bus2060 | 6.76 | 1.4
bus3001 | 10.83 | 13.02
bus3002 | 12.5 | 12.16
bus3003 | 12.5 | 12.85
bus3004 | 12.5 | 13.43
bus3005 | 13.36 | 12.85
bus3006 | 13.36 | 13.91
bus3007 | 13.36 | 14.71
bus3008 | 14.62 | 11.41
bus3009 | 14.61 | 12.04
bus3010 | 14.62 | 12.7
bus3011 | 14.61 | 13.36
bus3012 | 14.62 | 14.02
bus3013 | 14.61 | 10.77
bus3014 | 14.62 | 10.06
bus3015 | 15.79 | 11.41
bus3016 | 15.8 | 10.75
bus3017 | 15.8 | 10.1
bus3018 | 15.8 | 12.07
bus3019 | 15.8 | 12.72
bus3020 | 15.8 | 13.38
bus3021 | 15.8 | 14.03
bus3022 | 16.99 | 11.41
bus3023 | 16.99 | 10.76
bus3024 | 16.99 | 10.12
bus3025 | 16.99 | 9.47
bus3026 | 16.99 | 12.06
bus3027 | 16.99 | 12.72
bus3028 | 16.99 | 13.38
bus3029 | 16.99 | 14.03
bus3030 | 18.26 | 11.41
bus3031 | 18.26 | 10.91
bus3032 | 18.26 | 10.4
bus3033 | 18.26 | 9.9
bus3034 | 18.26 | 9.39
bus3035 | 18.25 | 12.05
bus3036 | 18.27 | 12.68
bus3037 | 18.25 | 13.32
bus3038 | 18.25 | 13.95
bus3039 | 18.26 | 14.59
bus3040 | 19.51 | 11.41
bus3041 | 19.51 | 10.87
bus3042 | 19.51 | 10.33
bus3043 | 19.51 | 9.79
bus3044 | 19.51 | 12.03
bus3045 | 19.51 | 12.63
bus3046 | 20.88 | 11.41
bus3047 | 20.88 | 12.16
bus3048 | 21.17 | 10.92
bus3049 | 22 | 10.92
bus3050 | 22.82 | 10.92
bus3051 | 23.64 | 10.92
bus3052 | 24.46 | 10.91
bus3053 | 19.51 | 14.79
bus3054 | 19.51 | 14.19
bus3055 | 21.01 | 14.79
bus3056 | 21.5 | 15.2
bus3057 | 22.22 | 15.2
bus3058 | 22.93 | 15.2
bus3059 | 23.65 | 15.2
bus3060 | 24.37 | 15.2
bus3061 | 25.09 | 15.2
bus3062 | 21.53 | 14.13
bus3063 | 22.24 | 14.13
bus3064 | 22.95 | 14.14
bus3065 | 23.66 | 14.13
bus3066 | 24.38 | 14.13
bus3067 | 25.09 | 14.13
bus3068 | 18.26 | 8.82
bus3069 | 16.65 | 8.82
bus3070 | 16.65 | 8.27
bus3071 | 16.65 | 7.71
bus3072 | 16.65 | 7.16
bus3073 | 15.76 | 8.82
bus3074 | 14.98 | 8.82
bus3075 | 19.05 | 8.82
bus3076 | 19.97 | 8.82
bus3077 | 20.73 | 8.82
bus3078 | 21.49 | 8.82
bus3079 | 19.97 | 8.07
bus3080 | 19.97 | 7.42
bus3081 | 19.21 | 7.42
bus3082 | 19.97 | 6.79
bus3083 | 19.1 | 6.79
bus3084 | 18.23 | 6.79
bus3085 | 17.36 | 6.79
bus3086 | 16.49 | 6.79
bus3087 | 15.62 | 6.79
bus3088 | 14.75 | 6.79
bus3089 | 13.88 | 6.79
bus3090 | 13.01 | 6.79
bus3091 | 12.14 | 6.79
bus3092 | 22.05 | 6.79
bus3093 | 22.07 | 7.3
bus3094 | 22.04 | 7.81
bus3095 | 22.05 | 8.32
bus3096 | 22.05 | 8.83
bus3097 | 22.05 | 9.34
bus3098 | 22.05 | 6.13
bus3099 | 22.05 | 5.56
bus3100 | 23.09 | 6.8
bus3101 | 23.86 | 6.8
bus3102 | 24.53 | 6.8
bus3103 | 25.12 | 6.8
bus3104 | 23.09 | 7.52
bus3105 | 23.08 | 8.08
bus3106 | 23.09 | 8.67
bus3107 | 19.98 | 5.54
bus3108 | 18.97 | 5.54
bus3109 | 18.07 | 5.54
bus3110 | 16.97 | 5.54
bus3111 | 15.97 | 5.54
bus3112 | 15.07 | 5.54
bus3113 | 18.63 | 4.76
bus3114 | 18.63 | 4.15
bus3115 | 18.63 | 3.53
bus3116 | 17.55 | 4.75
bus3117 | 16.55 | 4.76
bus3118 | 21.36 | 4.03
bus3119 | 22.77 | 4.03
bus3120 | 22.77 | 4.69
bus3121 | 22.78 | 5.34
bus3122 | 22.78 | 5.96
bus3123 | 23.64 | 4.04
bus3124 | 24.42 | 4.04
bus3125 | 25.17 | 4.04
bus3126 | 25.97 | 4.04
bus3127 | 25.97 | 4.58
bus3128 | 25.97 | 5.12
bus3129 | 25.97 | 5.66
bus3130 | 25.97 | 6.2
bus3131 | 25.97 | 6.75
bus3132 | 21.35 | 3.22
bus3133 | 21.36 | 2.41
bus3134 | 22.53 | 2.41
bus3135 | 23.57 | 2.41
bus3136 | 24.53 | 2.41
bus3137 | 21.37 | 1.79
bus3138 | 21.37 | 1.16
bus3139 | 21.36 | 0.53
bus3140 | 17.61 | 2.5
bus3141 | 18.42 | 2.48
bus3142 | 19.23 | 2.48
bus3143 | 20.03 | 2.49
bus3144 | 18.31 | 1.11
bus3145 | 18.99 | 1.11
bus3146 | 19.67 | 1.11
bus3147 | 20.35 | 1.11
bus3148 | 16.87 | 2.48
bus3149 | 16.13 | 2.48
bus3150 | 15.4 | 2.48
bus3151 | 14.66 | 2.48
bus3152 | 13.92 | 2.48
bus3153 | 13.18 | 2.48
bus3154 | 12.44 | 2.49
bus3155 | 11.7 | 2.49
bus3156 | 17.64 | 1.11
bus3157 | 16.9 | 1.11
bus3158 | 16.17 | 1.11
bus3159 | 15.43 | 1.11
bus3160 | 14.7 | 1.11
bus3161 | 13.97 | 1.11
bus3162 | 13.23 | 1.11